## Readme
Reference: AFT Fathom 10 - Examples - Pump Sizing and Selection with Flow Control Valves
Find: the pressure loss coefficient of the two control valves to allow a flowrate of 25 m³/h (0.0069444 m³/s) in each heat exchanger
R2022a
https://hydraucalc.com
Important notes: |  |  |  | The use of the HydrauCalcXL library imposes positive flowrates in all the branches of the studied system, |  |  |  | Description of the contents of the worksheet:
which requires knowing the direction of fluid flow in each branch.
• The input data is represented by the formatted cells as follows:
Before each new execution of the solver, it is advisable to replace the variable cells by the initial guesses.
|  |  |  | Sometimes the solver does not find a solution when it is restarted while keeping the variable cells | [5 empty] | Characteristics of the fluid:
resulting from the previous calculation.
Fluid flowrate imposed in each heat exchanger:
Characteristics of reservoirs:
Characteristics of pipes:
Description of the system:
The system is made up of:
|  | J1 Reservoir | [7 empty] | Characteristics of bend:
Name = Supply Tank
Liquid Surface Elevation = 1.5 meters
Liquid Surface Pressure = 0.7 barG (70 kPa-g)
Pipe Depth = 1.5 meters
J9 Reservoir
|  |  | Name = Receiving Tank | [6 empty] | Heat exchangers pressure loss:
Liquid Surface Elevation = 3 meters
Liquid Surface Pressure = 2 barG (200 kPa-g)
Pipe Depth for P5 and P9 (on Pipe Depth and Loss Coefficients tab) = 3 meters
J3 Tee
Elevation = 0 meters
Type = Simple
J6 Elbow
Elevation = 0 meters
Type = Standard
J4 Control Valve and J7 Control Valve
Elevation = 0 meters
|  |  | Valve Type = Flow Control (FCV) | [6 empty] | Pump head:
Volumetric Flow rate = 25 m3/hr
J5 Heat Exchanger and J8 Heat Exchanger
Elevation = 0 meters
Loss Model = Resistance Curve
Loss Curve Data = 0.7 bar (70 kPa) @ 25 m3/hr
Click "Fill as Quadratic" and then "Generate Curve Fit Now"
J2 Pump
Elevation = 0 meters
Type = Centrifugal, Sizing, Volumetric Flow Rate Fixed
Flow rate = 50 m3/hr
|  | Pipe Properties | [8 empty] | The pump head is only used in the graphic of the system working point.
All Pipes - Material = Steel - ANSI, Size = 2 inch, Type = STD (schedule 40), Friction Model = Standard
P1, P4, P6, P8 Length = 6 meters
|  |  | P2 Length = 15 meters | [5 empty] | • The calculations performed using the functions of the HydrauCalcXL add-in are represented by the cells formatted as follows:
|  |  | P3, P7 Length = 20 meters | [6 empty] | The functions used are recalled in gray text.
P5, P9 Length = 30 meters
Pressure loss in the components:
The assumptions are:
The characteristics of the fluid are known.
The heat exchangers flow rate is an input data.
The geometry of the components is known.
All the components are located in the same plane.
The pressure drop at the inlet and outlet of the tanks is neglected.
The pressure drop of the junction is neglected.
Resolution of problem:
In this calculation case, the determination of the pressure loss coefficients of the two control valves requires a certain number of iterations.
For this, we use Excel's equations solver (which requires the solver to be installed into Excel).
At each iteration, the pressure drop of all the components of the system is calculated using the functions integrated in HydrauCalcXL.
and the flowrate in each heat exchanger is compared to the requested flowrate.
The use of the solver for the pressure loss coefficients requires giving an estimate of the value of the coefficients.
When the solver does not find a solution to the problem, it is sometimes necessary to modify the initial guesses.
Remarks:
Pump static head:
Note 1:
Cells containing input data or calculated values are named using Excel's Name Manager.
This allows you to manipulate variable names in functions rather than cell addresses.
When the cell is named, the name of the cell is recalled to the left of it by a fuschia-colored text.
Example: cell E19 has the name "rho" which will be used in functions having density as a parameter.
Reservoir pressure:
| Note 2: | [8 empty] | Branchs head loss
A particular cell named "Cd" makes it possible, when setting up the functions for calculating the components,
to deactivate all error messages due to unspecified parameters which take the value 0 by default,
and which causes divisions by 0 (# DIV / 0!).
and data out of validity limits.
Reservoir static lift:
It is advised to assign the value 0 to this cell during the modelling of the system,
and the value 1 during the execution of the calculations.
Comparison of results with the reference:
• The calculations performed using functions built into Excel are represented by cells formatted as follows:
|  |  |  | Comparison of pressure loss coefficient | [5 empty] | The functions used are recalled in gray text.
|  |  |  | Name | Reference | HydrauCalcXL | Difference
|  |  |  | J4 | 9.0927 | 9.0109 | 0.8997% |  |  | Pump flowrate:
|  |  |  | J7 | 6.1587 | 6.0783 | 1.306%
Pump head (m fluid)
|  |  |  | Reference | HydrauCalcXL | Difference
|  |  |  | 55 | 54.9966 | -0.006214%
Branchs pressure loss:
Nodes static pressure:
System characteristic:
The pressure drop of the system is plotted by assuming a law in Q² from the operating point
• Solver data for finding a solution:
To use Solver, the problem can be viewed as a system of two equations
for two unknowns who are the pressure loss coefficients of each heat exchanger.
Two equations are needed to solve this system.
These equations are:
▪ P_n11 = P_J9 : the pressure at node 11 is equal to the tank pressure at the tank inlet
▪ P_n16 = P_J9 : the pressure at node 16 is equal to the tank pressure at the tank inlet
For our system, the initial guess of the pressure loss coefficients is fixed at 1.
In the present system, these initial guesses made it possible to find the solution:
[11 empty] | K_J4 | 0.1 | 1 | 10 | 20
[11 empty] | K_J7 | 0.1 | 1 | 10 | 20
The necessary data for the solver are:
the variable cells which, in our case, are the pressure loss coefficients of each heat exchanger K_J4 and K_J7 Q (cells W6 and W7),
the constraints to be respected (cells W9 and W10).
The following window is displayed if the solver find a solution.
The result obtained is presented in the following figure:

## System
Reference: AFT Fathom 10 - Examples - Pump Sizing and Selection with Flow Control Valves
Find: the pressure loss coefficient of the two control valves to allow a flowrate of 25 m³/h (0.0069444 m³/s) in each heat exchanger
R2022a | [13 empty] | Solver data
https://hydraucalc.com | [13 empty] | Value to be computed by solver (variable cells)
[14 empty] | J4 | K_J4 | 9.0109
Legend | [13 empty] | J7 | K_J7 | 6.0783
Input data | [13 empty] | Constraints
Excel calculation | [13 empty] | P_J9 - P_n11 = 0 |  | 0.0019531 | Pa | = P_J9 - P_n11
HydrauCalc calculation | [13 empty] | P_J9 - P_n16 = 0 |  | 0 | Pa | = P_J9 - P_n16
Variable name
Unit symbol | [13 empty] | Pump volume flowrate
Content of neighboring cell | [13 empty] | J2 | Q_J2 | 0.013889 | m³/s | = Q_J4 + Q_J7
Data verification | [13 empty] | Static pressure at node
Check data (0/1) |  | Cd | 1 | [10 empty] | n1 | P_n1 | 84682.1523 | Pa | = P_J1
[14 empty] | n2 | P_n2 | 37896.5664 | Pa | = P_n1 - dP_P1
Fluid data | [13 empty] | n3 | P_n3 | 576208.6914 | Pa | = P_n2 + P_J2
Density |  | rho | 998.1086 | kg/m³ | [9 empty] | n4 | P_n4 | 459244.7227 | Pa | = P_n3 - dP_P2
Kinematic Viscosity |  | nu | 9.802e-07 | m²/s | [9 empty] | n5 | P_n5 | 447076.4414 | Pa | = P_n4 - dP_P6
[14 empty] | n6 | P_n6 | 444183.5234 | Pa | = P_n5 - dP_J6
Volume flowrate | [13 empty] | n7 | P_n7 | 403622.5898 | Pa | = P_n6 - dP_P7
Name | [13 empty] | n8 | P_n8 | 372405.8887 | Pa | = P_n7 - dP_J7
J4 | Q_J4 | 0.0069444 | m³/s | [10 empty] | n9 | P_n9 | 360237.6074 | Pa | = P_n8 - dP_P8
J7 | Q_J7 | 0.0069444 | m³/s | [10 empty] | n10 | P_n10 | 290205.7012 | Pa | = P_n9 - dP_J8
[14 empty] | n11 | P_n11 | 229364.3027 | Pa | = P_n10 - dP_P9
Reservoir data | [13 empty] | n12 | P_n12 | 418683.7891 | Pa | = P_n4 - dP_P3
Name | Surface elevation (m) |  | Surface pressure (Pa) | [10 empty] | n13 | P_n13 | 372405.8906 | Pa | = P_n12 - dP_J4
J1 | H_J1 | 1.5 | Ps_J1 | 70000 | [9 empty] | n14 | P_n14 | 360237.6094 | Pa | = P_n13 - dP_P4
J9 | H_J9 | 3 | Ps_J9 | 200000 | [9 empty] | n15 | P_n15 | 290205.7031 | Pa | = P_n14 - dP_J5
[14 empty] | n16 | P_n16 | 229364.3047 | Pa | = P_n15 - dP_P5
Pipe data
Name | Diameter (m) |  | Length (m) |  | Absolute roughness (m) | [8 empty] | Reservoir static lift
P1 | D_P1 | 0.0525 | L_P1 | 6 | e_P1 | 4.572e-05 | [8 empty] | sL | 14.7814 | m fluid | = HeadLoss_dP_Rho_g(P_J9-P_J1;rho)
P2 | D_P2 | 0.0525 | L_P2 | 15 | e_P2 | 4.572e-05
P3 | D_P3 | 0.0525 | L_P3 | 20 | e_P3 | 4.572e-05 | [7 empty] | System characteristic
P4 | D_P4 | 0.0525 | L_P4 | 6 | e_P4 | 4.572e-05 | [7 empty] | Flowrate | Head
P5 | D_P5 | 0.0525 | L_P5 | 30 | e_P5 | 4.572e-05 | [7 empty] | m³/s | m fluid
P6 | D_P6 | 0.0525 | L_P6 | 6 | e_P6 | 4.572e-05 |  |  | Control valve pressure loss |  |  |  |  | 0 | 14.7814 | = sL + ( dH_1_4 / Q_J2^2 ) * V40^2 + ( dH_4_16 / Q_J4 ^2 ) * ( V40 / 2 )^2
P7 | D_P7 | 0.0525 | L_P7 | 20 | e_P7 | 4.572e-05 |  |  | J4 | dP_J4 | 46277.8984 | Pa | = PressureLoss_k_Qv_D_Rho(K_J4;Q_J4;D_P4;rho) | 0.0025 | 16.0844 | = sL + ( dH_1_4 / Q_J2^2 ) * V41^2 + ( dH_4_16 / Q_J4 ^2 ) * ( V41 / 2 )^2
P8 | D_P8 | 0.0525 | L_P8 | 6 | e_P8 | 4.572e-05 |  |  | J7 | dP_J7 | 31216.7012 | Pa | = PressureLoss_k_Qv_D_Rho(K_J7;Q_J7;D_P8;rho) | 0.005 | 19.9933 | = sL + ( dH_1_4 / Q_J2^2 ) * U42^2 + ( dH_4_16 / Q_J4 ^2 ) * ( U42 / 2 )^2
P9 | D_P9 | 0.0525 | L_P9 | 30 | e_P9 | 4.572e-05 | [7 empty] | 0.0075 | 26.5082 | = sL + ( dH_1_4 / Q_J2^2 ) * V43^2 + ( dH_4_16 / Q_J4 ^2 ) * ( V43 / 2 )^2
[9 empty] | Heat Exchanger pressure loss |  |  |  |  | 0.01 | 35.629 | = sL + ( dH_1_4 / Q_J2^2 ) * V44^2 + ( dH_4_16 / Q_J4 ^2 ) * ( V44 / 2 )^2
Bend data | [8 empty] | J5 | dP_J5 | 70031.9062 | Pa | = SplineInterpolation(Q_J4;B55:B62;$C$55:$C$62;Cd) | 0.0125 | 47.3557 | = sL + ( dH_1_4 / Q_J2^2 ) * V45^2 + ( dH_4_16 / Q_J4 ^2 ) * ( V45 / 2 )^2
Name | Diameter (m) |  | Curvature radius (m) |  | Angle (°) |  | Absolute roughness (m) |  | J8 | dP_J8 | 70031.9062 | Pa | = SplineInterpolation(Q_J7;B55:B62;C55:C62;Cd) | 0.015 | 61.6884 | = sL + ( dH_1_4 / Q_J2^2 ) * V46^2 + ( dH_4_16 / Q_J4 ^2 ) * ( V46 / 2 )^2
J6 | D_J6 | 0.0525 | C_J6 | 0.04 | A_J6 | 90 | e_J6 | 4.572e-05
Pipe pressure loss
Heat Exch J5 & J8 | [8 empty] | P1 | dP_P1 | 46785.5859 | Pa | = PipeStraightCircularCrossSection_dP(D_P1;L_P1;Q_J2;rho;nu;2;e_P1;;;Cd;L48)
Flowrate | Press. loss | [7 empty] | P2 | dP_P2 | 116963.9688 | Pa | = PipeStraightCircularCrossSection_dP(D_P2;L_P2;Q_J2;rho;nu;2;e_P2;;;Cd;L49)
m³/s | Pa | [7 empty] | P3 | dP_P3 | 40560.9336 | Pa | = PipeStraightCircularCrossSection_dP(D_P3;L_P3;Q_J4;rho;nu;2;e_P3;;;Cd;L50)
0 | 0 | [7 empty] | P4 | dP_P4 | 12168.2812 | Pa | = PipeStraightCircularCrossSection_dP(D_P4;L_P4;Q_J4;rho;nu;2;e_P4;;;Cd;L51)
0.0025 | 9072 | [7 empty] | P5 | dP_P5 | 60841.3984 | Pa | = PipeStraightCircularCrossSection_dP(D_P5;L_P5;Q_J4;rho;nu;2;e_P5;;;Cd;L52)
0.005 | 36288 | [7 empty] | P6 | dP_P6 | 12168.2812 | Pa | = PipeStraightCircularCrossSection_dP(D_P6;L_P6;Q_J7;rho;nu;2;e_P6;;;Cd;L53)
0.0075 | 81648 | [7 empty] | P7 | dP_P7 | 40560.9336 | Pa | = PipeStraightCircularCrossSection_dP(D_P7;L_P7;Q_J7;rho;nu;2;e_P7;;;Cd;L54)
0.01 | 145152 | [7 empty] | P8 | dP_P8 | 12168.2812 | Pa | = PipeStraightCircularCrossSection_dP(D_P8;L_P8;Q_J7;rho;nu;2;e_P8;;;Cd;L55)
0.0125 | 226800 | [7 empty] | P9 | dP_P9 | 60841.3984 | Pa | = PipeStraightCircularCrossSection_dP(D_P9;L_P9;Q_J7;rho;nu;2;e_P9;;;Cd;L56)
0.015 | 326592
0.0175 | 444528 | [7 empty] | Bend pressure loss
[9 empty] | J6 | dP_J6 | 2892.918 | Pa | =BendSmoothCircularCrossSection_dP(D_J6;F46;H46;e_J6;Q_J7;rho;nu;1;;;Cd;L59)
Pump head J2
Flowrate | Head | [7 empty] | Pump static head
m³/s | m fluid | [7 empty] | J2 | H_J2 | 54.9966 | m fluid | = SplineInterpolation(Q_J2;B67:B74;C67:C74;Cd)
0 | 60 | [7 empty] | J2 | P_J2 | 538312.125 | Pa | = StaticPressure_H_Rho_g(H_J2;rho)
0.005 | 59.928
0.01 | 57.912 | [7 empty] | Reservoir pressure at J2 level
0.015 | 53.952 | [7 empty] | J1 | P_J1 | 84682.1523 | Pa | = Ps_J1 + StaticPressure_H_Rho_g(H_J1;rho)
0.02 | 48.048 | [7 empty] | J9 | P_J9 | 229364.3047 | Pa | = Ps_J9 + StaticPressure_H_Rho_g(H_J9;rho)
0.025 | 40.2
0.03 | 30.408 | [7 empty] | Branchs pressure loss
0.035 | 18.672 | [7 empty] | n1 to 4 | dP_1_4 | 163749.5547 | Pa | = dP_P1 + dP_P2
[9 empty] | n4 to 16 | dP_4_16 | 229880.418 | Pa | = dP_P3 + dP_J4 + dP_P4 + dP_J5 + dP_P5
[9 empty] | n4 to 11 | dP_4_11 | 229880.4199 | Pa | = dP_P6 + dP_J6 + dP_J7 + dP_P7 + dP_P8 + dP_J8 + dP_P9
Branchs head loss
[9 empty] | n1 to 4 | dH_1_4 | 16.7295 | m fluid | = HeadLoss_dP_Rho_g(dP_1_4;rho)
[9 empty] | n4 to 16 | dH_4_16 | 23.4857 | m fluid | = HeadLoss_dP_Rho_g(dP_4_16;rho)
[9 empty] | n4 to 11 | dH_4_11 | 23.4857 | m fluid | = HeadLoss_dP_Rho_g(dP_4_11;rho)