## Readme
Reference: AFT Fathom 10 - Examples - Heat Exchanger System
Find: the volume flowrate in the loop
R2022a
https://hydraucalc.com
Important notes: |  |  |  | The use of the HydrauCalcXL library imposes positive flowrates in all the branches of the studied system, |  |  |  | Description of the contents of the worksheet:
which requires knowing the direction of fluid flow in each branch.
• The input data is represented by the formatted cells as follows:
Before each new execution of the solver, it is advisable to replace the variable cells by the initial guesses.
|  |  |  | Sometimes the solver does not find a solution when it is restarted while keeping the variable cells | [5 empty] | Characteristics of the fluid:
resulting from the previous calculation.
Pressure upstream of the pump:
Characteristics of pipes:
Description of the system:
Characteristics of bend:
The system is made up of:
Pump J5
Type = Centrifugal, Sizing, Volumetric Flow Rate
Flow rate = 25 m3/hr
6 meters @ 0 m3/hr
5.5 meters @ 25 m3/hr
3.5 meters @ 50 m3/hr
|  | Assigned Pressure J4 | [7 empty] | Heat exchangers pressure loss:
Pressure = 7 bar stagnation
Elbows J2, J3, J6, J7 (r/d = 0.8 r=8.180832)
All elbows are "Standard Elbows" with 90 degree bend
Pipe Properties
All Pipes - Material = Steel - ANSI, Size = 4 inch, Type = STD (schedule 40), Friction Model = Standard
Pipes P1, P5, P7
length = 60 meters
Pipes P3, P4
length = 30 meters
Pipes P2, P6
|  |  | length = 5 meters | [6 empty] | Pump head:
Heat Exchanger J1
25 m3/hr and 0.35 bar
The assumptions are:
The characteristics of the fluid are known.
Pressure in the loop imposed upstream of the pump
The geometry of the components is known.
All the components are located in the same plane.
The pump head is only used in the graphic of the system working point.
Resolution of problem:
• The calculations performed using the functions of the HydrauCalcXL add-in are represented by the cells formatted as follows:
| In this calculation case, the determination of the flowrate in the loop requires a certain number of iterations. | [8 empty] | The functions used are recalled in gray text.
For this, we use Excel's equations solver (which requires the solver to be installed into Excel).
Pressure loss in the components:
At each iteration, the pressure drop of all the components of the system is calculated using the functions integrated in HydrauCalcXL.
and the desired flowrate is reached when the pressures at nodes 1 and 14 have the same value.
The use of the solver for the flowrate giving an estimate of the value of the flowrate.
When the solver does not find a solution to the problem, it is sometimes necessary to modify the initial guesses.
Remarks:
Note 1:
Cells containing input data or calculated values are named using Excel's Name Manager.
This allows you to manipulate variable names in functions rather than cell addresses.
When the cell is named, the name of the cell is recalled to the left of it by a fuschia-colored text.
Example: cell E20 has the name "rho" which will be used in functions having density as a parameter.
| Note 2: | [8 empty] | Pump static head:
A particular cell named "Cd" makes it possible, when setting up the functions for calculating the components,
to deactivate all error messages due to unspecified parameters which take the value 0 by default,
and which causes divisions by 0 (# DIV / 0!).
and data out of validity limits.
• The calculations performed using functions built into Excel are represented by cells formatted as follows:
|  |  | It is advised to assign the value 0 to this cell during the modelling of the system, | [6 empty] | The functions used are recalled in gray text.
and the value 1 during the execution of the calculations.
Nodes static pressure:
Comparison of results with the reference:
Comparison of volume flowrate (m³/s)
|  |  |  | Name | Reference | HydrauCalcXL | Difference
|  |  |  | J5 | 0.0069611 | 0.0069649 | -0.0541%
System characteristic:
The pressure drop of the system is plotted by assuming a law in Q² from the operating point
Evolution of pressure in the loop:
• Solver data for finding a solution:
To use Solver, the problem can be viewed as a system of one equation
for one unknown who is the flowrate inthe loop.
In the present system, these initial guesses made it possible to find the solution:
[11 empty] | Q_J5 | 1e-05 | 0.0001 | 0.001 | 0.01
The necessary data for the solver are:
the variable cell which, in our case, is the flowrate in the loop Q_J5 (cell R8),
the constraint to be respected (cell R10).
The following window is displayed if the solver find a solution.
The result obtained is presented in the following figure:

## System
Reference: AFT Fathom 10 - Examples - Heat Exchanger System
Find: the volume flowrate in the loop
R2022a
https://hydraucalc.com
[13 empty] | Solver data |  |  |  |  | System
Legend | [12 empty] | Value to be computed by solver (variable cells): |  |  |  |  | Flowrate | Head
Input data | [12 empty] | J5 | Q_J5 | 0.0069649 | m²/s |  | m³/s | m fluid
Excel calculation | [12 empty] | Constraints |  |  |  |  | 0 | 0 | = ( H_J5 / Q_J5^2 ) * S54^2
HydrauCalc calculation | [12 empty] | P_n14 - P_n1 = 0 |  | 0.015686 | Pa | = P_n14 - P_n1 | 0.0025 | 0.70839 | = ( H_J5 / Q_J5^2 ) * S55^2
Variable name | [17 empty] | 0.005 | 2.8335 | = ( H_J5 / Q_J5^2 ) * S56^2
Unit symbol | [12 empty] | Static pressure at node |  |  |  |  | 0.0075 | 6.3755 | = ( H_J5 / Q_J5^2 ) * S57^2
Content of neighboring cell | [12 empty] | Name |  |  |  |  | 0.008 | 7.2539 | = ( H_J5 / Q_J5^2 ) * S58^2
[13 empty] | n1 | P_n1 | 700000 | Pa | = P_J4
Data verification | [12 empty] | n2 | P_n2 | 697850.3848 | Pa | = P_n1 - dP_P4
Check data (0/1) |  | Cd | 1 | [9 empty] | n3 | P_n3 | 751666.8496 | Pa | = P_n2 + P_J5
[13 empty] | n4 | P_n4 | 747367.6191 | Pa | = P_n3 - dP_P5
Fluid data | [12 empty] | n5 | P_n5 | 747174.5584 | Pa | = P_n4 - dP_J6
Fluid |  | Water 21 °C at 1 atm | [10 empty] | n6 | P_n6 | 746816.2892 | Pa | = P_n5 - dP_P6
Density |  | rho | 998.1086 | kg/m³ | [8 empty] | n7 | P_n7 | 746623.2285 | Pa | = P_n6 - dP_J7
Kinematic Viscosity |  | nu | 9.802e-07 | m²/s | [8 empty] | n8 | P_n8 | 742323.9981 | Pa | = P_n7 - dP_P7
[13 empty] | n9 | P_n9 | 707193.252 | Pa | = P_n8 - dP_J1
Pressure | [12 empty] | n10 | P_n10 | 702894.0215 | Pa | = P_n9 - dP_P1
Name | [12 empty] | n11 | P_n11 | 702700.9608 | Pa | = P_n10 - dP_J2
J4 | P_J4 | 700000 | Pa | [9 empty] | n12 | P_n12 | 702342.6916 | Pa | = P_n11 - dP_P2
[13 empty] | n13 | P_n13 | 702149.6309 | Pa | = P_n12 - dP_J3
Pipe data | [12 empty] | n14 | P_n14 | 700000.0157 | Pa | = P_n13 - dP_P3
Name | Diameter (m) |  | Length (m) |  | Absolute roughness (m) |  |  |  | Pump Head |  | 0
P1 | D_P1 | 0.1023 | L_P1 | 60 | e_P1 | 4.572e-05 |  |  | J5 | H_J5 | 5.4982 | m fluid | = SplineInterpolation(Q_J5;$B$57:$B$64;$C$57:$C$64;Cd)
P2 | D_P2 | 0.1023 | L_P2 | 5 | e_P2 | 4.572e-05 |  |  | J5 | P_J5 | 53816.4648 | Pa | = StaticPressure_H_Rho_g(H_J5;rho)
P3 | D_P3 | 0.1023 | L_P3 | 30 | e_P3 | 4.572e-05
P4 | D_P4 | 0.1023 | L_P4 | 30 | e_P4 | 4.572e-05 |  |  | Heat Exchanger pressure loss
P5 | D_P5 | 0.1023 | L_P5 | 60 | e_P5 | 4.572e-05 |  |  | J1 | dP_J1 | 35130.7461 | Pa | = SplineInterpolation(Q_J5;$B$45:$B$52;$C$45:$C$52;Cd)
P6 | D_P6 | 0.1023 | L_P6 | 5 | e_P6 | 4.572e-05
P7 | D_P7 | 0.1023 | L_P7 | 60 | e_P7 | 4.572e-05 |  |  | Pipe pressure loss
[9 empty] | P1 | dP_P1 | 4299.2305 | Pa | = PipeStraightCircularCrossSection_dP(D_P1;L_P1;Q_J5;rho;nu;2;e_P1;;;Cd;L36)
Bend data | [8 empty] | P2 | dP_P2 | 358.2692 | Pa | = PipeStraightCircularCrossSection_dP(D_P2;L_P2;Q_J5;rho;nu;2;e_P2;;;Cd;L37)
Name | Diameter (m) |  | Curvature radius (m) |  | Angle (°) |  | Absolute roughness (m) |  | P3 | dP_P3 | 2149.6152 | Pa | = PipeStraightCircularCrossSection_dP(D_P3;L_P3;Q_J5;rho;nu;2;e_P3;;;Cd;L38)
J2 | D_J2 | 0.1023 | C_J2 | 0.08184 | A_J2 | 90 | e_J2 | 4.572e-05 | P4 | dP_P4 | 2149.6152 | Pa | = PipeStraightCircularCrossSection_dP(D_P4;L_P4;Q_J5;rho;nu;2;e_P4;;;Cd;L39)
J3 | D_J3 | 0.1023 | C_J3 | 0.08184 | A_J3 | 90 | e_J3 | 4.572e-05 | P5 | dP_P5 | 4299.2305 | Pa | = PipeStraightCircularCrossSection_dP(D_P5;L_P5;Q_J5;rho;nu;2;e_P5;;;Cd;L40)
J6 | D_J6 | 0.1023 | C_J6 | 0.08184 | A_J6 | 90 | e_J6 | 4.572e-05 | P6 | dP_P6 | 358.2692 | Pa | = PipeStraightCircularCrossSection_dP(D_P6;L_P6;Q_J5;rho;nu;2;e_P6;;;Cd;L41)
J7 | D_J7 | 0.1023 | C_J7 | 0.08184 | A_J7 | 90 | e_J7 | 4.572e-05 | P7 | dP_P7 | 4299.2305 | Pa | = PipeStraightCircularCrossSection_dP(D_P7;L_P7;Q_J5;rho;nu;2;e_P7;;;Cd;L42)
Heat Exchanger J1 | [8 empty] | Bend pressure loss
Flowrate | Press. loss | [7 empty] | J2 | dP_J2 | 193.0607 | Pa | = BendSmoothCircularCrossSection_dP(D_J2;C_J2;A_J2;e_J2;Q_J5;rho;nu;Cd;;;;L45)
m³/s | Pa | [7 empty] | J3 | dP_J3 | 193.0607 | Pa | = BendSmoothCircularCrossSection_dP(D_J3;C_J3;A_J3;e_J3;Q_J5;rho;nu;Cd;;;;L46)
0 | 0 | [7 empty] | J6 | dP_J6 | 193.0607 | Pa | = BendSmoothCircularCrossSection_dP(D_J6;C_J6;A_J6;e_J6;Q_J5;rho;nu;1Cd;;;;L47)
0.002 | 2903 | [7 empty] | J7 | dP_J7 | 193.0607 | Pa | = BendSmoothCircularCrossSection_dP(D_J7;C_J7;A_J7;e_J7;Q_J5;rho;nu;1Cd;;;;L48)
0.004 | 11612
0.006 | 26127
0.008 | 46448
0.01 | 72576
Pump J5
Flowrate | Press. loss
m³/s | m fluid
0 | 6
0.0025 | 5.9928
0.005 | 5.7912
0.0075 | 5.3952
0.01 | 4.8048