## Readme
Reference: AFT Fathom 10 - Examples - Hot Water System
Find: the pressure loss coefficient of the control valve to allow a flowrate of 70 m³/h (0.01944 m³/s) in each heat exchanger and the working point of the pumps
R2022a
https://hydraucalc.com
Important notes: |  |  |  | The use of the HydrauCalcXL library imposes positive flowrates in all the branches of the studied system, |  |  |  |  | Description of the contents of the worksheet:
which requires knowing the direction of fluid flow in each branch.
• The input data is represented by the formatted cells as follows:
Before each new execution of the solver, it is advisable to replace the variable cells by the initial guesses.
|  |  |  | Sometimes the solver does not find a solution when it is restarted while keeping the variable cells | [6 empty] | Characteristics of the fluid:
resulting from the previous calculation.
Fluid flowrate imposed in each heat exchanger and the reservoir:
Characteristics of reservoirs:
Characteristics of pipes:
Description of the system:
The system is made up of:
|  | Pipes P1, P2, P13 |  |  |  |  | Pipes P5, P10
|  |  | 6 inch |  |  |  |  | 4 inch
|  |  | Length = 3 meters |  |  |  |  | Length = 1 meter
|  | Pipes P3, P7, P11, P15, P19 |  |  |  |  | Pipes P17, P21
|  |  | 4 inch |  |  |  |  | 4 inch
|  |  | Length = 3 meters |  |  |  |  | Length = 5 meters
|  | Pipe P24 |  |  |  |  | Pipes P14, P23
|  |  | 6 inch |  |  |  |  | 6 inch
|  |  | Length = 1.5 meters |  |  |  |  | Length = 9 meters
|  | Pipes P4, P8, P12, P16, P18, P20, P22 |  |  |  |  | Reservoir J1
|  |  | 4 inch |  |  |  |  | Liquid Surface Elevation = 3 meters
|  |  | Length = 1.5 meters |  |  |  |  | Liquid Surface Pressure = 0 barG (0 kPa-g)
|  | Pipes P6, P9 | [5 empty] | Pipe Depth = 3 meters
|  |  | 6 inch |  |  |  | Control Valves J14, J17
|  |  | Length = 1 meter |  |  |  |  | Type = Flow Control (FCV) |  |  | Characteristics of bend:
Control Setpoint = 70 m3/hr
The assumptions are:
The characteristics of the fluid are known.
The heat exchangers flowrate is an input data.
The geometry of the components is known.
All the components are located in the same plane.
The pressure drop of the junctions is neglected.
The pressure in the loop is imposed upstream of the pump by the reservoir.
Resolution of problem: | [10 empty] | Heat exchangers pressure loss:
In this calculation case, the determination of the pressure loss coefficients of the two control valves
and the flowrate of the pumps requires a certain number of iterations.
For this, we use Excel's equations solver (which requires the solver to be installed into Excel).
The system has 4 unknowns. these are the pressure drop coefficients of the control valves and the flow rates of two of the three pumps.
The flow rate of the third pump will be the result of the difference between the flow rates of the two exchangers and the flow rates of the two pumps.
To solve this system of equations with four unknowns, four equations are needed.
In the studied system these equations are the equality of the pressures at the level of the junctions with meeting of the currents J2, J8, J11 and J20:
- at junction J2 equal pressures at nodes 2 and 33,
- at junction J8 equal pressure at nodes 8 and 12,
|  | - at junction J11 equal pressure at nodes 13 and 18, | [8 empty] | Pumps head:
- at junction J20 equal pressure at nodes 30 and 38.
These equations are introduced into the solver in the form of constraints to be respected.
At each iteration, the pressure drop of all the components of the system is calculated using the functions integrated in HydrauCalcXL.
and the flows are compared to the requested flows.
The use of the solver for the flows and pressure loss coefficients requires giving an estimate of the value.
When the solver does not find a solution to the problem, it is sometimes necessary to modify the initial guesses.
Remarks:
Note 1:
Cells containing input data or calculated values are named using Excel's Name Manager.
|  | This allows you to manipulate variable names in functions rather than cell addresses. | [7 empty] | • The calculations performed using the functions of the HydrauCalcXL add-in are represented by the cells formatted as follows:
|  | When the cell is named, the name of the cell is recalled to the left of it by a fuschia-colored text. | [8 empty] | The functions used are recalled in gray text.
Example: cell E20 has the name "rho" which will be used in functions having density as a parameter.
Pressure loss in the components:
Note 2:
A particular cell named "Cd" makes it possible, when setting up the functions for calculating the components,
to deactivate all error messages due to unspecified parameters which take the value 0 by default,
and which causes divisions by 0 (# DIV / 0!).
and data out of validity limits.
It is advised to assign the value 0 to this cell during the modelling of the system,
and the value 1 during the execution of the calculations.
Comparison of results with the reference:
Comparison of volume flowrate (m³/s)
|  |  |  | Name | Reference | HydrauCalcXL | Difference
|  |  |  | J4 | 0.012872 | 0.012896 | -0.1845%
|  |  |  | J7 | 0.013144 | 0.01302 | 0.9436%
|  |  |  | J10 | 0.012872 | 0.012973 | -0.7791%
Comparison of pressure loss coefficient
|  |  |  | Name | Reference | HydrauCalcXL | Difference
|  |  |  | J14 | 9.964 | 9.9443 | 0.1978%
|  |  |  | J17 | 8.752 | 8.8609 | -1.244%
Pump static head:
Reservoir pressure:
• The calculations performed using functions built into Excel are represented by cells formatted as follows:
The functions used are recalled in gray text.
Nodes static pressure:
Deducted volume flowrate:
• Solver data for finding a solution:
To use Solver, the problem can be viewed as a system of four equations
for four unknowns who are the pressure loss coefficients of the two control valves J14 et J17
and the flowrate of the two pumps J4 and J7. The flowrate of the third pump J10 is deducted.
In the present system, these initial guesses made it possible to find the solution:
[12 empty] | Q_J4 | 0.01 | 0.015
[12 empty] | Q_J7 | 0.01 | 0.015
[12 empty] | K_J14 | 10 | 100
[12 empty] | K_J17 | 10 | 100
The necessary data for the solver are:
▪ the variable cells which, in our case, are
- the flowrate of the pumps J4 and J7 (cells Y8 and Y9),
- the pressure loss coefficients the heat exchangers J14 and J17 (cells Y10 and Y11),
▪ the constraints to be respected (cells Y13 to Y16).
[11 empty] | Note: | The initial guess of the flowrate of each pump must take into account the total flowrate of the exchangers, which is 140 m³/h.
And therefore the flowrate of each of the three pumps will be close to 140/3 or approximately 46.7 m³/h (0.013 m³/s).
An initial guess greater than 70m³/h (0.01944 m³/s) for the J4 and J7 pumps will generate a negative flow for the J10 pump and cause an error.
The following window is displayed if the solver find a solution.
The result obtained is presented in the following figure:

## System
Reference: AFT Fathom 10 - Examples - Hot Water System
Find: the pressure loss coefficient of the control valve to allow a flowrate of 70 m³/h (0.01944 m³/s) in each heat exchanger and the working point of the pumps
R2022a
https://hydraucalc.com
Solver data
Legend | [13 empty] | Value to be computed by solver (variable cells)
Input data | [13 empty] | J4 | Q_J4 | 0.012896 | m³/s
Excel calculation | [13 empty] | J7 | Q_J7 | 0.01302 | m³/s
HydrauCalc calculation | [13 empty] | J14 | K_J14 | 9.9443
Variable name | [13 empty] | J17 | K_J17 | 8.8609
Unit symbol | [13 empty] | Constraints:
Content of neighboring cell | [13 empty] | P_n33 - P_n2 = 0 |  | -0.016941 | Pa | = P_n33 - P_n2
[14 empty] | P_n8 - P_n12 = 0 |  | 0.012405 | Pa | = P_n8 - P_n12
Data verification | [13 empty] | P_n18 - P_n13 = 0 |  | 3.8124 | Pa | = P_n18 - P_n13
Check data (0/1) |  | Cd | 1 | [10 empty] | P_n38 - P_n30 = 0 |  | -0.0019531 | Pa | = P_n38 - P_n30
Fluid data
Fluid |  | Water 66 °C at 1 atm | [11 empty] | Deducted volume flowrate
Density |  | rho | 979.93 | kg/m³ | [9 empty] | Name
Kinematic Viscosity |  | nu | 4.408e-07 | m²/s | [9 empty] | P9 | Q_P9 | 0.025916 | m³/s | = Q_J4 + Q_J7
[14 empty] | P13 | Q_P13 | 0.038889 | m³/s | = Q_J4 + Q_J7 + Q_J10
Volume flowrate | [13 empty] | J10 | Q_J10 | 0.012973 | m³/s | = Q_J14 + Q_J17 - Q_J4 - Q_J7
Name | [13 empty] | P6 | Q_P6 | 0.025993 | m³/s | = Q_J7 + Q_J10
J14 | Q_J14 | 0.019444 | m³/s | [10 empty] | P23 | Q_P23 | 0.038889 | m³/s | = Q_J14 + Q_J17
J17 | Q_J17 | 0.019444 | m³/s
P1 | Q_P1 | 1e-05 | m³/s | [10 empty] | Static pressure at node
Name
Reservoir data | [13 empty] | n1 | P_n1 | 130154.4922 | Pa | = P_J1
Name | Surface elevation (m) |  | Surface pressure (Pa) |  | K flow outlet | [8 empty] | n2 | P_n2 | 130154.4913 | Pa | = P_n1 - dP_P1
J1 | H_J1 | 3 | Ps_J1 | 101325 | K_J1 | 0 | [7 empty] | n3 | P_n3 | 129495.118 | Pa | = P_n2 - dP_P2
[14 empty] | n4 | P_n4 | 128869.3531 | Pa | = P_n3 - dP_P3
Pipe data | [13 empty] | n5 | P_n5 | 229378.2594 | Pa | = P_n4 + P_J4
Name | Diameter (m) |  | Length (m) |  | Absolute roughness (m) | [8 empty] | n6 | P_n6 | 229065.377 | Pa | = P_n5 - dP_P4
P1 | D_P1 | 0.15405 | L_P1 | 3 | e_P1 | 4.572e-05 |  |  | Control valve pressure loss |  |  |  |  | n7 | P_n7 | 228715.3237 | Pa | = P_n6 - dP_J5
P2 | D_P2 | 0.15405 | L_P2 | 3 | e_P2 | 4.572e-05 |  |  | J14 | dP_J14 | 27309.9082 | Pa | = PressureLoss_k_Qv_D_Rho(K_J14;Q_J14;D_P15;rho) | n8 | P_n8 | 228506.7354 | Pa | = P_n7 - dP_P5
P3 | D_P3 | 0.10226 | L_P3 | 3 | e_P3 | 4.572e-05 |  |  | J17 | dP_J17 | 24334.543 | Pa | = PressureLoss_k_Qv_D_Rho(K_J17;Q_J17;D_P19;rho) | n9 | P_n9 | 129394.4202 | Pa | = P_n3 - dP_P6
P4 | D_P4 | 0.10226 | L_P4 | 1.5 | e_P4 | 4.572e-05 | [7 empty] | n10 | P_n10 | 128756.9294 | Pa | = P_n9 - dP_P7
P5 | D_P5 | 0.10226 | L_P5 | 1 | e_P5 | 4.572e-05 |  |  | Control valve flow coefficient Kv |  |  |  |  | n11 | P_n11 | 228825.4684 | Pa | = P_n10 + P_J7
P6 | D_P6 | 0.15405 | L_P6 | 1 | e_P6 | 4.572e-05 |  |  | J14 |  | 132.6823 |  | = FlowCoefficientKv_Qv_dP_Rho(Q_J14;dP_J14;rho) | n12 | P_n12 | 228506.723 | Pa | = P_n11 - dP_P8
P7 | D_P7 | 0.10226 | L_P7 | 3 | e_P7 | 4.572e-05 |  |  | J17 |  | 140.5599 |  | = FlowCoefficientKv_Qv_dP_Rho(Q_J17;dP_J17;rho) | n13 | P_n13 | 228406.5962 | Pa | = P_n12 - dP_P9
P8 | D_P8 | 0.10226 | L_P8 | 1.5 | e_P8 | 4.572e-05 | [7 empty] | n14 | P_n14 | 129183.4322 | Pa | = P_n9 - dP_P10
P9 | D_P9 | 0.15405 | L_P9 | 1 | e_P9 | 4.572e-05 |  |  | Heat Exchanger pressure loss |  |  |  |  | n15 | P_n15 | 129120.9638 | Pa | = P_n14 - dP_J9
P10 | D_P10 | 0.10226 | L_P10 | 1 | e_P10 | 4.572e-05 |  |  | J15 | dP_J15 | 62520.543 | Pa | = SplineInterpolation(Q_J14;D71:D78;E71:E78;Cd) | n16 | P_n16 | 128488 | Pa | = P_n15 - dP_P11
P11 | D_P11 | 0.10226 | L_P11 | 3 | e_P11 | 4.572e-05 |  |  | J18 | dP_J18 | 62520.543 | Pa | = SplineInterpolation(Q_J17;D71:D78;E71:E78;Cd) | n17 | P_n17 | 228726.8906 | Pa | = P_n16 + P_J10
P12 | D_P12 | 0.10226 | L_P12 | 1.5 | e_P12 | 4.572e-05 | [7 empty] | n18 | P_n18 | 228410.4087 | Pa | = P_n17 - dP_P12
P13 | D_P13 | 0.15405 | L_P13 | 3 | e_P13 | 4.572e-05 |  |  | Pipe pressure loss |  |  |  |  | n19 | P_n19 | 227751.0354 | Pa | = P_n18 - dP_P13
P14 | D_P14 | 0.15405 | L_P14 | 9 | e_P14 | 4.572e-05 |  |  | P1 | dP_P1 | 0.00093748 | Pa | = PipeStraightCircularCrossSection_dP(D_P1;L_P1;Q_P1;rho;nu;2;e_P1;;;Cd;L48) | n20 | P_n20 | 227196.8945 | Pa | = P_n19 - dP_J12
P15 | D_P15 | 0.10226 | L_P15 | 3 | e_P15 | 4.572e-05 |  |  | P2 | dP_P2 | 659.3733 | Pa | = PipeStraightCircularCrossSection_dP(D_P2;L_P2;Q_P23;rho;nu;2;e_P2;;;Cd;L49) | n21 | P_n21 | 225218.7745 | Pa | = P_n20 - dP_P14
P16 | D_P16 | 0.10226 | L_P16 | 1.5 | e_P16 | 4.572e-05 |  |  | P3 | dP_P3 | 625.7648 | Pa | = PipeStraightCircularCrossSection_dP(D_P3;L_P3;Q_J4;rho;nu;2;e_P3;;;Cd;L50) | n22 | P_n22 | 224524.2236 | Pa | = P_n21 - dP_P18
P17 | D_P17 | 0.15405 | L_P17 | 5 | e_P17 | 4.572e-05 |  |  | P4 | dP_P4 | 312.8824 | Pa | = PipeStraightCircularCrossSection_dP(D_P4;L_P4;Q_J4;rho;nu;2;e_P4;;;Cd;L51) | n23 | P_n23 | 223731.0929 | Pa | = P_n22 - dP_J16
P18 | D_P18 | 0.10226 | L_P18 | 1.5 | e_P18 | 4.572e-05 |  |  | P5 | dP_P5 | 208.5883 | Pa | = PipeStraightCircularCrossSection_dP(D_P5;L_P5;Q_J4;rho;nu;2;e_P5;;;Cd;L52) | n24 | P_n24 | 222341.9911 | Pa | = P_n23 - dP_P19
P19 | D_P19 | 0.10226 | L_P19 | 3 | e_P19 | 4.572e-05 |  |  | P6 | dP_P6 | 100.6978 | Pa | = PipeStraightCircularCrossSection_dP(D_P6;L_P6;Q_P6;rho;nu;2;e_P6;;;Cd;L53) | n25 | P_n25 | 198007.4481 | Pa | = P_n24 - dP_J17
P20 | D_P20 | 0.10226 | L_P20 | 1.5 | e_P20 | 4.572e-05 |  |  | P7 | dP_P7 | 637.4908 | Pa | = PipeStraightCircularCrossSection_dP(D_P7;L_P7;Q_J7;rho;nu;2;e_P7;;;Cd;L54) | n26 | P_n26 | 197312.8972 | Pa | = P_n25 - dP_P20
P21 | D_P21 | 0.15405 | L_P21 | 5 | e_P21 | 4.572e-05 |  |  | P8 | dP_P8 | 318.7454 | Pa | = PipeStraightCircularCrossSection_dP(D_P8;L_P8;Q_J7;rho;nu;2;e_P8;;;Cd;L55) | n27 | P_n27 | 134792.3542 | Pa | = P_n26 - dP_J18
P22 | D_P22 | 0.10226 | L_P22 | 1.5 | e_P22 | 4.572e-05 |  |  | P9 | dP_P9 | 100.1268 | Pa | = PipeStraightCircularCrossSection_dP(D_P9;L_P9;Q_P9;rho;nu;2;e_P9;;;Cd;L56) | n28 | P_n28 | 134504.1035 | Pa | = P_n27 - dP_P21
P23 | D_P23 | 0.15405 | L_P23 | 9 | e_P23 | 4.572e-05 |  |  | P10 | dP_P10 | 210.988 | Pa | = PipeStraightCircularCrossSection_dP(D_P10;L_P10;Q_J10;rho;nu;2;e_P10;;;Cd;L57) | n29 | P_n29 | 133710.9727 | Pa | = P_n28 - dP_J19
P24 | D_P24 | 0.15405 | L_P24 | 1.5 | e_P24 | 4.572e-05 |  |  | P11 | dP_P11 | 632.9639 | Pa | = PipeStraightCircularCrossSection_dP(D_P11;L_P11;Q_J10;rho;nu;2;e_P11;;;Cd;L58) | n30 | P_n30 | 133016.4218 | Pa | = P_n29 - dP_P22
[9 empty] | P12 | dP_P12 | 316.4819 | Pa | = PipeStraightCircularCrossSection_dP(D_P12;L_P12;Q_J10;rho;nu;2;e_P12;;;Cd;L59) | n31 | P_n31 | 131038.3018 | Pa | = P_n30 - dP_P23
Bend data | [8 empty] | P13 | dP_P13 | 659.3733 | Pa | = PipeStraightCircularCrossSection_dP(D_P13;L_P13;Q_P13;rho;nu;2;e_P13;;;Cd;L60) | n32 | P_n32 | 130484.161 | Pa | = P_n31 - dP_J21
Name | Diameter (m) |  | Curvature radius (m) |  | Angle (°) |  | Absolute roughness (m) |  | P14 | dP_P14 | 1978.12 | Pa | = PipeStraightCircularCrossSection_dP(D_P14;L_P14;Q_P13;rho;nu;2;e_P14;;;Cd;L61) | n33 | P_n33 | 130154.4743 | Pa | = P_n32 - dP_P24
J5 | D_J5 | 0.10226 | C_J5 | 0.15339 | A_J5 | 90 | e_J5 | 4.572e-05 | P15 | dP_P15 | 1389.1018 | Pa | = PipeStraightCircularCrossSection_dP(D_P15;L_P15;Q_J14;rho;nu;2;e_P15;;;Cd;L62) | n34 | P_n34 | 223829.6727 | Pa | = P_n21 - dP_P15
J9 | D_J9 | 0.15405 | C_J9 | 0.23108 | A_J9 | 90 | e_J9 | 4.572e-05 | P16 | dP_P16 | 694.5509 | Pa | = PipeStraightCircularCrossSection_dP(D_P16;L_P16;Q_J14;rho;nu;2;e_P16;;;Cd;L63) | n35 | P_n35 | 196519.7645 | Pa | = P_n34 - dP_J14
J12 | D_J12 | 0.15405 | C_J12 | 0.23108 | A_J12 | 90 | e_J12 | 4.572e-05 | P17 | dP_P17 | 288.2508 | Pa | = PipeStraightCircularCrossSection_dP(D_P17;L_P17;Q_J14;rho;nu;2;e_P17;;;Cd;L64) | n36 | P_n36 | 195825.2136 | Pa | = P_n35 - dP_P16
J16 | D_J16 | 0.10226 | C_J16 | 0.15339 | A_J16 | 90 | e_J16 | 4.572e-05 | P18 | dP_P18 | 694.5509 | Pa | = PipeStraightCircularCrossSection_dP(D_P18;L_P18;Q_J17;rho;nu;2;e_P18;;;Cd;L65) | n37 | P_n37 | 133304.6706 | Pa | = P_n36 - dP_J15
J19 | D_J19 | 0.10226 | C_J19 | 0.15339 | A_J19 | 90 | e_J19 | 4.572e-05 | P19 | dP_P19 | 1389.1018 | Pa | = PipeStraightCircularCrossSection_dP(D_P19;L_P19;Q_J17;rho;nu;2;e_P19;;;Cd;L66) | n38 | P_n38 | 133016.4199 | Pa | = P_n37 - dP_P17
J21 | D_J21 | 0.15405 | C_J21 | 0.23108 | A_J21 | 90 | e_J21 | 4.572e-05 | P20 | dP_P20 | 694.5509 | Pa | = PipeStraightCircularCrossSection_dP(D_P20;L_P20;Q_J17;rho;nu;2;e_P20;;;Cd;L67)
[9 empty] | P21 | dP_P21 | 288.2508 | Pa | = PipeStraightCircularCrossSection_dP(D_P21;L_P21;Q_J17;rho;nu;2;e_P21;;;Cd;L68)
Heat Exch J15 & J18 | [8 empty] | P22 | dP_P22 | 694.5509 | Pa | = PipeStraightCircularCrossSection_dP(D_P22;L_P22;Q_J17;rho;nu;2;e_P22;;;Cd;L69)
Flowrate | Press. loss | [7 empty] | P23 | dP_P23 | 1978.12 | Pa | = PipeStraightCircularCrossSection_dP(D_P23;L_P23;Q_P23;rho;nu;2;e_P23;;;Cd;L70)
m³/s | Pa | [7 empty] | P24 | dP_P24 | 329.6866 | Pa | = PipeStraightCircularCrossSection_dP(D_P24;L_P24;Q_P23;rho;nu;2;e_P24;;;Cd;L71)
0 | 0
0.005 | 1246 | [7 empty] | Bend pressure loss
0.01 | 12761 | [7 empty] | J5 | dP_J5 | 350.0533 | Pa | = BendSmoothCircularCrossSection_dP(D_J5;C_J5;A_J5;e_J5;Q_J4;rho;nu;1;;;Cd;L74)
0.015 | 34545 | [7 empty] | J9 | dP_J9 | 62.4684 | Pa | = BendSmoothCircularCrossSection_dP(D_J9;C_J9;A_J5;e_J9;Q_J10;rho;nu;1;;;Cd;L75)
0.02 | 66596 | [7 empty] | J12 | dP_J12 | 554.1409 | Pa | = BendSmoothCircularCrossSection_dP(D_J12;C_J12;A_J12;e_J5;Q_P13;rho;nu;1;;;Cd;L76)
0.025 | 108916 | [7 empty] | J16 | dP_J16 | 793.1307 | Pa | = BendSmoothCircularCrossSection_dP(D_J16;C_J16;A_J16;e_J16;Q_J17;rho;nu;1;;;Cd;L77)
0.03 | 161503 | [7 empty] | J19 | dP_J19 | 793.1307 | Pa | = BendSmoothCircularCrossSection_dP(D_J19;C_J19;A_J19;e_J19;Q_J17;rho;nu;1;;;Cd;L78)
0.035 | 224359 | [7 empty] | J21 | dP_J21 | 554.1409 | Pa | = BendSmoothCircularCrossSection_dP(D_J21;C_J21;A_J21;e_J21;Q_P23;rho;nu;1;;;Cd;L79)
Pumps head | [8 empty] | Pumps head
Flowrate | Head | [7 empty] | J4 | H_J4 | 10.459 | m fluid | = SplineInterpolation(Q_J4;D83:D90;E83:E90;Cd)
m³/s | m fluid | [7 empty] | J7 | H_J7 | 10.4131 | m fluid | = SplineInterpolation(Q_J7;D83:D90;E83:E90;Cd)
0 | 11.48 | [7 empty] | J10 | H_J10 | 10.4309 | m fluid | = SplineInterpolation(Q_J10;D83:D90;E83:E90;Cd)
0.0025 | 11.86
0.005 | 11.97 | [7 empty] | Pumps pressure
0.0075 | 11.79 | [7 empty] | J4 | P_J4 | 100508.9062 | Pa | = PressureLoss_dH_Rho_g(H_J4;rho)
0.01 | 11.33 | [7 empty] | J7 | P_J7 | 100068.5391 | Pa | = PressureLoss_dH_Rho_g(H_J7;rho)
0.0125 | 10.6 | [7 empty] | J10 | P_J10 | 100238.8906 | Pa | = PressureLoss_dH_Rho_g(H_J10;rho)
0.015 | 9.58
0.0175 | 8.28 | [7 empty] | Reservoir pressure
[9 empty] | J1 | P_J1 | 130154.4922 | Pa | = Ps_J1 + StaticPressure_H_Rho_g(H_J1;rho)