## Readme
Reference: Internal Flow Systems - 2ed - D.S. Miller (1990) - Simple system - Fig. 3.1 - page 28
Find: the pump head and the system working point
R2022a
https://hydraucalc.com
Important note: |  |  |  | The use of the HydrauCalcXL library imposes positive flowrates in all the branches of the studied system, |  |  | Description of the contents of the worksheet:
which requires knowing the direction of fluid flow in each branch.
• The input data is represented by the formatted cells as follows:
Characteristics of the fluid:
Fluid flowrate imposed in the system:
Characteristics of system components:
Description of the system:
The studied system is a simplified system for understanding the calculation method.
The system is made up of:
• a reservoir inlet,
• a pipe inlet,
• a pump,
• a reflux valve,
• a pipe outlet,
• a reservoir outlet.
The assumptions are:
The pump flowrate is an input data.
The characteristics of the fluid are known.
The geometry of the components is known.
The roughness of the piping is defined by a Darcy coefficient of friction.
All the components are located in the same plane.
|  | The calculation method used is that of Miller. | [6 empty] | Fluid levels in reservoirs:
Resolution of problem:
Extended Bernoulli equation for a real fluid:
Pump characteristic curve:
with:
hP Pump head
hL Head loss
VA » 0
VB » 0
PA = PB
and so:
The calculation consists in determining the pressure drop of each element of the system
and to add them to obtain the pressure drop of all the components.
The pump head is only used in the graphic of the system working point.
• The calculations performed using the functions of the HydrauCalcXL add-in are represented by the cells formatted as follows:
| The functions integrated into HydrauCalcXL allow you to calculate explicitly (direct calculation without iterations) | [7 empty] | The functions used are recalled in gray text.
the pressure drop of the components as a function of:
|  |  | • the fluid flow rate, | [5 empty] | Pressure loss in the components:
• the characteristics of the fluid,
• the geometry of the components.
The units used by default in the HydrauCalcXL functions are those of the International System (SI units).
Remarks:
Note 1:
Cells containing input data or calculated values are named using Excel's Name Manager.
This allows you to manipulate variable names in functions rather than cell addresses.
When the cell is named, the name of the cell is recalled to the left of it by a fuschia-colored text.
Example: cell E20 has the name "rho" which will be used in functions having density as a parameter.
• The calculations performed using functions built into Excel are represented by cells formatted as follows:
The functions used are recalled in gray text.
Note 2:
A particular cell named "Cd" makes it possible, when setting up the functions for calculating the components,
to deactivate all error messages due to:
unspecified parameters which take the value 0 by default and which causes divisions by 0 (# DIV / 0!),
and data out of validity limits.
It is advised to assign the value 0 to this cell during the modelling of the system,
and the value 1 during the execution of the calculations.
The pressure drop of the system is plotted by assuming a law in Q² from the operating point
Comparison of results with the reference:
Total pressure loss (Pa)
|  |  |  | Reference | HydrauCalcXL | Difference
|  |  |  | 211000 | 210898.7806 | -0.04797%
Pump head (m fluid)
|  |  |  | Reference | HydrauCalcXL | Difference
|  |  |  | 28.6 | 28.5057 | -0.3298%

## Fixed Flow
Reference: Internal Flow Systems - 2ed - D.S. Miller (1990) - Simple system - Fig. 3.1 - page 28
Find: the pump head and the system working point
R2022a | [12 empty] | Total pressure loss
https://hydraucalc.com | [12 empty] | dP | 210898.7806 | Pa | = dP_E1 + dP_P1 + dP_V1 + dP_P2 + dP_D1
Total head loss
Legend | [12 empty] | hL | 21.5057 | m fluid | = HeadLoss_dP_Rho_g(dP;rho)
Input data
Excel calculation | [12 empty] | Static lift
HydrauCalc calculation | [12 empty] | sL | 7 | m fluid | = H_R2 - H_R1
Variable name
Unit symbol | [12 empty] | Pump head |  | 0
Content of neighboring cell | [12 empty] | hP | 28.5057 | m fluid | = sL + hL
Data verification
Check data (0/1) |  | Cd | 1 | [9 empty] | System characteristic
[13 empty] | Flowrate | Head
Fluid data (Water 20°C) | [12 empty] | m³/s | m fluid
Density |  | rho | 1000 | kg/m³ | [8 empty] | 0 | 7 | = sL + ( hL / Q^2 ) * 0^2
Kinematic Viscosity |  | nu | 1.1e-06 | m²/s | [8 empty] | 0.5 | 7.7109 | = sL + ( hL / Q^2 ) * 0.5^2
[8 empty] | Pipe pressure loss (Pa) |  |  |  |  | 1 | 9.8437 | = sL + ( hL / Q^2 ) * 1^2
Volume flow rate | [7 empty] | P1 | dP_P1 | 8275.4072 | Pa | = PipeStraightCircularCrossSection_dP(D_P1;L_P1;Q;rho;nu;6;;f_P1;;Cd;J23) | 1.5 | 13.3984 | = sL + ( hL / Q^2 ) * 1.5^2
| Q | 2.75 | m³/s |  |  |  |  | P2 | dP_P2 | 179587.8281 | Pa | = PipeStraightCircularCrossSection_dP(D_P2;L_P2;Q;rho;nu;6;;f_P2;;Cd;J24) | 2 | 18.3749 | = sL + ( hL / Q^2 ) * 2^2
[13 empty] | 2.5 | 24.7733 | = sL + ( hL / Q^2 ) * 2.5^2
Pipe data | [7 empty] | System entrance (Pa) |  |  |  |  | 3 | 32.5935 | = sL + ( hL / Q^2 ) * 3^2
Name | Diameter (m) |  | Length (m) |  | Darcy friction factor |  |  | E1 | dP_E1 | 587.0677 | Pa | = EntranceFlushMountedRounded_dP(D_E1;R_E1;Q;rho;nu;2;Cd;J27)
P1 | D_P1 | 1 | L_P1 | 90 | f_P1 | 0.015
P2 | D_P2 | 0.8 | L_P2 | 640 | f_P2 | 0.015 |  | Reflux valve (Pa)
[8 empty] | V1 | dP_V1 | 7482.8262 | Pa | = PressureLoss_k_Qv_D_Rho(K_V1;Q;D_V1;rho)
Reflux valve
Name | Diameter (m) |  | Pressure loss coef. |  |  |  |  | System discharge (Pa)
V1 | D_V1 | 0.8 | K_V1 | 0.5 |  |  |  | D1 | dP_D1 | 14965.6514 | Pa | = DischargeFlushMountedSharpEdged_dP(D_D1;Q;rho;nu;2;Cd;J33)
System entrance (rounded entrance)
Name | Diameter (m) |  | Round radius (m) |  |  |  | Pump characteristic
E1 | D_E1 | 1 | R_E1 | 0.09 |  |  | Flowrate | Head
[7 empty] | m³/s | m fluid
System discharge (sharp-edged discharge) | [6 empty] | 0 | 33.1226
Name | Diameter (m) | [5 empty] | 0.5 | 32.8258
D1 | D_D1 | 0.8 |  |  |  |  | 1 | 32.3643
[7 empty] | 1.5 | 31.7586
Reservoir data | [6 empty] | 2 | 30.7083
Name | Surface elevation (m) | [5 empty] | 2.5 | 29.4326
R1 | H_R1 | 1.5 |  |  |  |  | 3 | 27.2112
R2 | H_R2 | 8.5 |  |  |  |  | 3.5 | 22.8132