## Readme
Reference: Internal Flow Systems - 2ed - D.S. Miller (1990) - Simple system - Fig. 3.1 - page 28
Find: the flowrate and the system working point
R2022a
https://hydraucalc.com
Important notes: |  |  | The use of the HydrauCalcXL library imposes positive flowrates in all the branches of the studied system, |  | Description of the contents of the worksheet:
which requires knowing the direction of fluid flow in each branch.
The differences compared to the "Tutorial 1 - System pressure loss calculation.xlsx" file are as follows:
Before each new execution of the solver, it is advisable to replace the variable cells by the initial guesses.
|  |  | Sometimes the solver does not find a solution when it is restarted while keeping the variable cells |  |  |  | Pump head imposed in the system (input data):
resulting from the previous calculation.
Solver data for finding a solution:
To use Solver, the problem can be viewed as a system of one equation
for one unknown who is the Flowrate.
For our system, the initial guess is fixed at 1 m³/s
Description of the system:
The studied system is a simplified system for understanding the calculation method.
In the present system, these initial guesses made it possible to find the solution:
The system is made up of:
|  | • a reservoir inlet, | [6 empty] | Q | 0.5 | 1 | 5 | 10
• a pipe inlet,
|  | • a pump, | [5 empty] | The necessary data for the solver are:
|  | • a reflux valve, | [6 empty] | the variable cell which, in our case, is the desired flow Q (cell V6),
|  | • a pipe outlet, | [6 empty] | the constraint to be respected (cell V8).
• a reservoir outlet.
The assumptions are:
The pump head is an input data.
The characteristics of the fluid are known.
The geometry of the components is known.
The roughness of the piping is defined by a Darcy coefficient of friction.
All the components are located in the same plane.
The calculation method used is that of Miller.
Resolution of problem:
In this calculation case, the determination of the fluid flowrate in the system requires a certain number of iterations.
For this, we use Excel's equations solver (which requires the solver to be installed into Excel).
At each iteration, the pressure drop of all the components of the system is calculated using the functions integrated in HydrauCalcXL.
and the total resistance of the system is compared to the pump load.
The use of the solver for the flowrate search requires giving an estimate of the value of the flow.
When the solver does not find a solution to the problem, it is sometimes necessary to modify the initial guesse.
The following window is displayed if the solver find a solution.
The result obtained is presented in the following figure:

## Fixed pump head
Reference: Internal Flow Systems - 2ed - D.S. Miller (1990) - Simple system - Fig. 3.1 - page 28
Find: the flowrate and the system working point
R2022a | [12 empty] | Solver data
https://hydraucalc.com | [12 empty] | Value to be computed by solver (variable cells):
[13 empty] | Flowrate | Q | 2.756 | m²/s
Legend | [12 empty] | Constraints:
Input data | [12 empty] | hP - hL - sL = 0 |  | 0.00015221 | Pa | = hP - hL - sL
Excel calculation
HydrauCalc calculation | [12 empty] | Total pressure loss
Variable name | [12 empty] | dP | 211822.1523 | Pa | = dP_E1 + dP_P1 + dP_V1 + dP_P2 + dP_D1
Unit symbol
Content of neighboring cell | [12 empty] | Total head loss
[13 empty] | hL | 21.5998 | m fluid | =HeadLoss_dP_Rho_g(dP;rho)
Data verification | [12 empty] | Static lift
Check data (0/1) |  | Cd | 1 | [9 empty] | sL | 7 | m fluid | = H_R2 - H_R1
Fluid data (Water 20°C) | [12 empty] | System characteristic
Density |  | rho | 1000 | kg/m³ | [8 empty] | Flowrate | Head
Kinematic Viscosity |  | nu | 1.1e-06 | m²/s | [8 empty] | m³/s | m fluid
[8 empty] | Pipe pressure loss (Pa) |  |  |  |  | 0 | 7 | = sL + ( hL / Q^2 ) * 0^2
Pump head |  | 0 | [5 empty] | P1 | dP_P1 | 8311.6396 | Pa | = PipeStraightCircularCrossSection_dP(D_P1;L_P1;Q;rho;nu;6;;f_P1;;Cd;J23) | 0.5 | 7.7109 | = sL + ( hL / Q^2 ) * 0.5^2
| hP | 28.6 | m fluid |  |  |  |  | P2 | dP_P2 | 180374.1094 | Pa | = PipeStraightCircularCrossSection_dP(D_P2;L_P2;Q;rho;nu;6;;f_P2;;Cd;J24) | 1 | 9.8437 | = sL + ( hL / Q^2 ) * 1^2
[13 empty] | 1.5 | 13.3984 | = sL + ( hL / Q^2 ) * 1.5^2
Pipe data | [7 empty] | System entrance (Pa) |  |  |  |  | 2 | 18.3749 | = sL + ( hL / Q^2 ) * 2^2
Name | Diameter (m) |  | Length (m) |  | Darcy friction factor |  |  | E1 | dP_E1 | 589.6381 | Pa | = EntranceFlushMountedRounded_dP(D_E1;R_E1;Q;rho;nu;2;Cd;J27) | 2.5 | 24.7733 | = sL + ( hL / Q^2 ) * 2.5^2
P1 | D_P1 | 1 | L_P1 | 90 | f_P1 | 0.015 | [6 empty] | 3 | 32.5935 | = sL + ( hL / Q^2 ) * 3^2
P2 | D_P2 | 0.8 | L_P2 | 640 | f_P2 | 0.015 |  | Reflux valve (Pa)
[8 empty] | V1 | dP_V1 | 7515.5884 | Pa | = PressureLoss_k_Qv_D_Rho(K_V1;Q;D_V1;rho)
Reflux valve
Name | Diameter (m) |  | Pressure loss coef. |  |  |  |  | System discharge (Pa)
V1 | D_V1 | 0.8 | K_V1 | 0.5 |  |  |  | D1 | dP_D1 | 15031.1768 | Pa | = DischargeFlushMountedSharpEdged_dP(D_D1;Q;rho;nu;2;Cd;J33)
System entrance (rounded entrance)
Name | Diameter (m) |  | Round radius (m) |  |  |  | Pump characteristic
E1 | D_E1 | 1 | R_E1 | 0.09 |  |  | Flowrate | Head
[7 empty] | m³/s | m fluid
System discharge (sharp-edged discharge) | [6 empty] | 0 | 33.1226
Name | Diameter (m) | [5 empty] | 0.5 | 32.8258
D1 | D_D1 | 0.8 |  |  |  |  | 1 | 32.3643
[7 empty] | 1.5 | 31.7586
Reservoir data | [6 empty] | 2 | 30.7083
Name | Surface elevation (m) | [5 empty] | 2.5 | 29.4326
R1 | H_R1 | 1.5 |  |  |  |  | 3 | 27.2112
R2 | H_R2 | 8.5 |  |  |  |  | 3.5 | 22.8132