## Readme
Reference: Flomaster - Example: Marine Cooling System
Find: diameter of each orifice plate to meet the required flowrate through the various branches
R2023a
https://hydraucalc.com
Important notes: |  |  |  | The use of the HydrauCalcXL library imposes positive flowrates in all the branches of the studied system, |  |  |  | Description of the contents of the worksheet:
which requires knowing the direction of fluid flow in each branch.
• The input data is represented by the formatted cells as follows:
Before each new execution of the solver, it is advisable to replace the variable cells by the initial guesses.
|  |  |  | Sometimes the solver does not find a solution when it is restarted while keeping the variable cells | [5 empty] | Characteristics of the fluid:
resulting from the previous calculation.
Fluid flowrate imposed in each heat exchanger and the reservoir:
Characteristics of the reservoir:
Characteristics of pipes:
Description of the system:
The system is made up of:
5 Heat Exchangers HE11, HE12, HE20, HE21, HE31
5 Restriction orifices plate OP5, OP6, OP44, OP45, OP47
24 Pipes P7, P8, P9, P10, P13, P15, P16, P17, P18, P19, P22, P25, P26, P27, P28, P29, P30, P32, P33, P34, P35, P42, P48, P51
10 Junctions J14, J41, J43, J46, J49, J50, J52, J53, J55, J56
3 Dividing Sharp-Edged Junctions J41, J46, J53
4 Combining Sharp-Edged Junctions J50, J52, J55, J56
2 Symetric Dividing Sharp-Edged T-Junctions J14, J49
|  |  | 1 Symetric Combining Sharp-Edged T-Junction J43 | [6 empty] | Characteristics of orifices plate:
1 Pump Pp36
1 Reservoir R37
The assumptions are:
The heat exchangers flowrate is an input data.
The characteristics of the fluid are known.
The pressure in the loop is imposed upstream of the pump by the reservoir.
|  | The geometry of the components is known. | [7 empty] | Characteristics of junctions:
All the components are located in the same plane.
This example also shows the method to take into account the pressure drop of the T-junctions.
Resolution of problem:
In this calculation case, the determination of the diameter of the five restriction orifices requires a certain number of iterations.
For this, we use Excel's equations solver (which requires the solver to be installed into Excel).
At each iteration, the pressure drop of all the components of the system is calculated using the functions integrated in HydrauCalcXL.
and the flowrate in each heat exchanger is compared to the requested flowrate.
The use of the solver for the orifice diameters requires giving an estimate of the value of the diameters.
When the solver does not find a solution to the problem, it is sometimes necessary to modify the initial guesses.
Characteristics of heat-exchangers:
Because the direction of flow of the fluid must be known in each branch,
one of the difficulties of this system is to know the direction of flow in the pipes 33, 34 and 35.
This example has been processed under Flowmaster and therefore the direction of flow of all the branches is known.
When this case arises, it may be necessary to modify the circuit modeling if the solver does not find solutions.
In this example, the flow directions are as follows:
Pumps head:
Remarks:
Note 1:
Cells containing input data or calculated values are named using Excel's Name Manager.
This allows you to manipulate variable names in functions rather than cell addresses.
When the cell is named, the name of the cell is recalled to the left of it by a fuschia-colored text.
|  | Example: cell E19 has the name "rho" which will be used in functions having density as a parameter. | [6 empty] | • The calculations performed using the functions of the HydrauCalcXL add-in are represented by the cells formatted as follows:
The functions used are recalled in gray text.
Pressure loss in the components:
Note 2:
A particular cell named "Cd" makes it possible, when setting up the functions for calculating the components,
to deactivate all error messages due to unspecified parameters which take the value 0 by default,
and which causes divisions by 0 (# DIV / 0!).
and data out of validity limits.
It is advised to assign the value 0 to this cell during the modelling of the system,
and the value 1 during the execution of the calculations.
Comparison of results with the reference:
Comparison of orifices diameters (m)
|  |  |  | Name | Reference | HydrauCalcXL | Difference
|  |  |  | OP5 | 0.0689 | 0.069713 | -1.18%
|  |  |  | OP6 | 0.1014 | 0.10306 | -1.638%
|  |  |  | OP44 | 0.09371 | 0.097034 | -3.547%
|  |  |  | OP45 | 0.0937 | 0.097034 | -3.558%
|  |  |  | OP47 | 0.07349 | 0.074531 | -1.417%
Comparison of flowrate (m³/s)
|  |  |  | Name | Reference | HydrauCalcXL | Difference
|  |  |  | P28 | 0.01373 | 0.013814 | -0.6106%
Pump static head:
• The calculations performed using functions built into Excel are represented by cells formatted as follows:
The functions used are recalled in gray text.
Nodes static pressure:
Deducted volume flowrate:
• Solver data for finding a solution:
The problem can be viewed as a system of six equations and six unknowns.
The necessary data for the solver are:
▪ the variable cells (the six unknowns) which, in our case, are:
- the diameters of the five orifices plate OP5, OP6, OP44, OP45, OP47 (cells Q8 to Q12),
- the flowrate in the pipe P28 (cell Q13),
▪ the constraints (the six équations) to be respected which are:
- at node 30: equal pressure from node 1 and that generated by reservoir R37 (cell Q15),
- at nodes 43, 54, 51, 53 and 23: at the exit of the combining junctions, equality of the pressures coming from the two input branches (cells Q16 to Q20),
Additional constraints can be imposed to facilitate the solution of the system which are:
▪ the diameter of the orifices must be less than or equal to the internal diameter of the pipe.
In the following figure, cells Q21 to Q25 are comments to list all the constraints taken into account.
In the present system, these initial guesses made it possible to find a solution:
[11 empty] | Do_ | 0.07705 | m
[11 empty] | Do_ | 0.07705 | m
[11 empty] | Do_ | 0.07705 | m
[11 empty] | Do_ | 0.07705 | m
[11 empty] | Do_ | 0.07705 | m
[11 empty] | Q_28 | 0.01 | m³/s
The initial guesses are taken equal:
half the inside diameter of the pipe for the diameter of the orifices,
to the value of the flow in exchanger number 12 for the flow in branch number 28.
The solver parameters are presented in the following figure:
The following window is displayed if the solver find a solution.
The result obtained is presented in the following figure:
Before each new execution of the solver, it is advisable to replace the variable cells (Q8 to Q13) by the initial guesses.
Sometimes the solver does not find a solution when it is restarted while keeping the variable cells resulting from the previous calculation.

## System
Reference: Flomaster - Example: Marine Cooling System
Find: the diameter of each orifice plate to meet the required flowrate through the various branches
R2023a
https://hydraucalc.com
[7 empty] | Solver data |  |  |  |  | Pressure loss of each component
Legend | [6 empty] | Value to be computed by solver (variable cells):
Input data | [6 empty] | OP5 | Do_OP5 | 0.069713 | m |  | Heat Exchanger pressure loss:
Excel calculation | [6 empty] | OP6 | Do_OP6 | 0.10306 | m |  | HE11 | dP_HE11 | 56.2453 | Pa | =PressureLoss_k_Qv_D_Rho(K_HE11;Q_11;D_HE11;Rho)
HydrauCalc calculation | [6 empty] | OP44 | Do_OP44 | 0.097034 | m |  | HE12 | dP_HE12 | 56.2453 | Pa | =PressureLoss_k_Qv_D_Rho(K_HE12;Q_12;D_HE12;Rho)
Variable name | [6 empty] | OP45 | Do_OP45 | 0.097034 | m |  | HE20 | dP_HE20 | 92.9769 | Pa | =PressureLoss_k_Qv_D_Rho(K_HE20;Q_20;D_HE20;Rho)
Unit symbol | [6 empty] | OP47 | Do_OP47 | 0.074531 | m |  | HE21 | dP_HE21 | 92.9769 | Pa | =PressureLoss_k_Qv_D_Rho(K_HE21;Q_21;D_HE21;Rho)
Content of neighboring cell | [6 empty] | P28 | Q_28 | 0.013814 | m³/s |  | HE31 | dP_HE31 | 64.5673 | Pa | =PressureLoss_k_Qv_D_Rho(K_HE31;Q_31;D_HE31;Rho)
Constraints:
Data verification | [6 empty] | P_n30_R37 - P_n30_n1 = 0 |  | 0.0031052 | Pa | = P_n30_R37 - P_n30_n1 | Orifice plate pressure loss:
Check data (0/1) |  | Cd | 0 |  |  |  | P_n43_n38 - P_n43_n39 = 0 |  | 0 | Pa | = P_n43_n38 - P_n43_n39 | OP5 | dP_OP5 | 13516.2725 | Pa | =OrificeSharpEdgedCircularCrossSection_dP(Dpi_OP5;Do_OP5;Q_11;Rho;Nu;2;Cd;Z16)
[7 empty] | P_n54_n50 - P_n54_n28 = 0 |  | 0.20667 | Pa | = P_n54_n50 - P_n54_n28 | OP6 | dP_OP6 | 1767.5093 | Pa | =OrificeSharpEdgedCircularCrossSection_dP(Dpi_OP6;Do_OP6;Q_12;Rho;Nu;2;Cd;Z17)
Fluid data (Water 20°C) | [6 empty] | P_n51_n47 - P_n51_n48 = 0 |  | 0.0018005 | Pa | = P_n51_n47 - P_n51_n48 | OP44 | dP_OP44 | 4171.7217 | Pa | =OrificeSharpEdgedCircularCrossSection_dP(Dpi_OP44;Do_OP44;Q_20;Rho;Nu;2;Cd;Z18)
Density |  | Rho | 998.2061 | kg/m³ |  |  | P_n53_n29 - P_n53_n55 = 0 |  | -0.0024014 | Pa | = P_n53_n29 - P_n53_n55 | OP45 | dP_OP45 | 4171.7217 | Pa | =OrificeSharpEdgedCircularCrossSection_dP(Dpi_OP45;Do_OP45;Q_21;Rho;Nu;2;Cd;Z19)
Kinematic Viscosity |  | Nu | 1.0034e-06 | m²/s |  |  | P_n23_n58 - P_n23_n59 = 0 |  | -0.00089073 | Pa | = P_n23_n58 - P_n23_n59 | OP47 | dP_OP47 | 11310.8838 | Pa | =OrificeSharpEdgedCircularCrossSection_dP(Dpi_OP47;Do_OP47;Q_31;Rho;Nu;2;Cd;Z20)
Do_OP5 ≤ D_P51
Imposed volume flowrate (Heat-Exchangers) | [6 empty] | Do_OP6 ≤ D_P10 |  |  |  |  | Pipe pressure loss:
|  | Q_11 | 0.014 | m³/s |  |  | Do_OP44 ≤ D_P16 |  |  |  |  | P7 | dP_P7 | 22305.6133 | Pa | =PipeStraightCircularCrossSection_dP(D_P7;L_P7;Q_36;Rho;Nu;5;e_P7;;;Cd;Z23;Z23)
|  | Q_12 | 0.014 | m³/s |  |  | Do_OP45 ≤ D_P15 |  |  |  |  | P8 | dP_P8 | 31227.8555 | Pa | =PipeStraightCircularCrossSection_dP(D_P8;L_P8;Q_36;Rho;Nu;5;e_P8;;;Cd;Z24;Z24)
|  | Q_20 | 0.018 | m³/s |  |  | Do_OP47 ≤ D_P48 |  |  |  |  | P9 | dP_P9 | 26766.7363 | Pa | =PipeStraightCircularCrossSection_dP(D_P9;L_P9;Q_36;Rho;Nu;5;e_P9;;;Cd;Z25;Z25)
|  | Q_21 | 0.018 | m³/s | [7 empty] | P10 | dP_P10 | 1097.9087 | Pa | =PipeStraightCircularCrossSection_dP(D_P10;L_P10;Q_12;Rho;Nu;5;e_P10;;;Cd;Z26;Z26)
|  | Q_31 | 0.015 | m³/s | [7 empty] | P13 | dP_P13 | 1537.0721 | Pa | =PipeStraightCircularCrossSection_dP(D_P13;L_P13;Q_11;Rho;Nu;5;e_P13;;;Cd;Z27;Z27)
[7 empty] | Deducted flowrate: |  |  |  |  | P15 | dP_P15 | 357.6075 | Pa | =PipeStraightCircularCrossSection_dP(D_P15;L_P15;Q_21;Rho;Nu;5;e_P15;;;Cd;Z28;Z28)
Reservoir 37 | [7 empty] | Q_36 | 0.065 | m³/s | = Q_11 + Q_20 + Q_21 + Q_31 | P16 | dP_P16 | 357.6075 | Pa | =PipeStraightCircularCrossSection_dP(D_P16;L_P16;Q_20;Rho;Nu;5;e_P16;;;Cd;Z29;Z29)
Liquid level above base |  | Rllab | 1 | m |  |  |  | Q_42 | 0.036 | m³/s | = Q_21 + Q_20 | P17 | dP_P17 | 357.6075 | Pa | =PipeStraightCircularCrossSection_dP(D_P17;L_P17;Q_21;Rho;Nu;5;e_P17;;;Cd;Z30;Z30)
Base level above ref. |  | Rblar | 0 | m |  |  |  | Q_29 | 0.029 | m³/s | = Q_36 - Q_42 | P18 | dP_P18 | 357.6075 | Pa | =PipeStraightCircularCrossSection_dP(D_P18;L_P18;Q_20;Rho;Nu;5;e_P18;;;Cd;Z31;Z31)
Surface pressure |  | Rsp | 100000 | Pa |  |  |  | Q_19 | 0.036 | m³/s | = Q_21 + Q_20 | P19 | dP_P19 | 2778.2522 | Pa | =PipeStraightCircularCrossSection_dP(D_P19;L_P19;Q_19;Rho;Nu;5;e_P19;;;Cd;Z32;Z32)
[8 empty] | Q_26 | 0.027814 | m³/s | = Q_12 + Q_28 | P22 | dP_P22 | 1097.9087 | Pa | =PipeStraightCircularCrossSection_dP(D_P22;L_P22;Q_12;Rho;Nu;5;e_P22;;;Cd;Z33;Z33)
Pipe data | [7 empty] | Q_27 | 0.027814 | m³/s | = Q_12 + Q_28 | P25 | dP_P25 | 658.7452 | Pa | =PipeStraightCircularCrossSection_dP(D_P25;L_P25;Q_11;Rho;Nu;5;e_P25;;;Cd;Z34;Z34)
Name | Diameter (m) |  | Length (m) |  | Absolute roughness (m) |  |  | Q_33 | 0.013814 | m³/s | = Q_26 - Q_11 | P26 | dP_P26 | 1673.6257 | Pa | =PipeStraightCircularCrossSection_dP(D_P26;L_P26;Q_26;Rho;Nu;5;e_P26;;;Cd;Z35;Z35)
P7 | D_P7 | 0.1541 | L_P7 | 25 | e_P7 | 0.00025 |  | Q_34 | 0.0011862 | m³/s | = Q_31 - Q_33 | P27 | dP_P27 | 1673.6257 | Pa | =PipeStraightCircularCrossSection_dP(D_P27;L_P27;Q_27;Rho;Nu;5;e_P27;;;Cd;Z36;Z36)
P8 | D_P8 | 0.1541 | L_P8 | 35 | e_P8 | 0.00025 |  | Q_35 | 0.037186 | m³/s | = Q_19 + Q_34 | P28 | dP_P28 | 3209.5027 | Pa | =PipeStraightCircularCrossSection_dP(D_P28;L_P28;Q_28;Rho;Nu;5;e_P28;;;Cd;Z37;Z37)
P9 | D_P9 | 0.1541 | L_P9 | 30 | e_P9 | 0.00025 | [5 empty] | P29 | dP_P29 | 4541.2417 | Pa | =PipeStraightCircularCrossSection_dP(D_P29;L_P29;Q_29;Rho;Nu;5;e_P29;;;Cd;Z38;Z38)
P10 | D_P10 | 0.1541 | L_P10 | 25 | e_P10 | 0.00025 | [5 empty] | P30 | dP_P30 | 1003.8947 | Pa | =PipeStraightCircularCrossSection_dP(D_P30;L_P30;Q_31;Rho;Nu;5;e_P30;;;Cd;Z39;Z39)
P13 | D_P13 | 0.1541 | L_P13 | 35 | e_P13 | 0.00025 | Pressure at nodes: |  |  |  |  | P32 | dP_P32 | 752.9211 | Pa | =PipeStraightCircularCrossSection_dP(D_P32;L_P32;Q_31;Rho;Nu;5;e_P32;;;Cd;Z40;Z40)
P15 | D_P15 | 0.1541 | L_P15 | 5 | e_P15 | 0.00025 | n23 | P_n23_n58 | 171123.1128 | Pa | = P_n22 - dPb_J53 - dP_P28 - dPb_J56 | P33 | dP_P33 | 1069.8342 | Pa | =PipeStraightCircularCrossSection_dP(D_P33;L_P33;Q_33;Rho;Nu;5;e_P33;;;Cd;Z41;Z41)
P16 | D_P16 | 0.1541 | L_P16 | 5 | e_P16 | 0.00025 | n23 | P_n23_n59 | 171123.1137 | Pa | = P_n22 - dPt_J53 - dP_P10 - dP_HE12 - dP_OP6 - dP_P22 - dPt_J56 | P34 | dP_P34 | 11.0777 | Pa | =PipeStraightCircularCrossSection_dP(D_P34;L_P34;Q_34;Rho;Nu;5;e_P34;;;Cd;Z42;Z42)
P17 | D_P17 | 0.1541 | L_P17 | 5 | e_P17 | 0.00025 | [5 empty] | P35 | dP_P35 | 7403.3022 | Pa | =PipeStraightCircularCrossSection_dP(D_P35;L_P35;Q_35;Rho;Nu;5;e_P35;;;Cd;Z43;Z43)
P18 | D_P18 | 0.1541 | L_P18 | 5 | e_P18 | 0.00025 | n30 | P_n30_R37 | 109789.0586 | Pa | = Rsp + StaticPressure_H_Rho_g(Rllab + Rblar;Rho) | P42 | dP_P42 | 2778.2522 | Pa | =PipeStraightCircularCrossSection_dP(D_P42;L_P42;Q_42;Rho;Nu;5;e_P42;;;Cd;Z44;Z44)
P19 | D_P19 | 0.1541 | L_P19 | 10 | e_P19 | 0.00025 | n30 | P_n30_n1 | 109789.0555 | Pa | = P_n53_29 - dP_P9 - dP_P8 | P48 | dP_P48 | 752.9211 | Pa | =PipeStraightCircularCrossSection_dP(D_P48;L_P48;Q_31;Rho;Nu;5;e_P48;;;Cd;Z45;Z45)
P22 | D_P22 | 0.1541 | L_P22 | 25 | e_P22 | 0.00025 | [5 empty] | P51 | dP_P51 | 439.1635 | Pa | =PipeStraightCircularCrossSection_dP(D_P51;L_P51;Q_11;Rho;Nu;5;e_P51;;;Cd;Z46;Z46)
P25 | D_P25 | 0.1541 | L_P25 | 15 | e_P25 | 0.00025 | n43 | P_n43_n38 | 182980.8613 | Pa | = P_n12 - dPl_J14 - dP_P16 - dP_HE20 - dP_OP44 - dP_P18 - dPl_J43
P26 | D_P26 | 0.1541 | L_P26 | 10 | e_P26 | 0.00025 | n43 | P_n43_n39 | 182980.8613 | Pa | = P_n12 - dPr_J14 - dP_P15 - dP_HE21 - dP_OP45 - dP_P17 - dPr_J43 | Junction pressure loss (Pa):
P27 | D_P27 | 0.1541 | L_P27 | 10 | e_P27 | 0.00025 | [5 empty] | Through (Pa)
P28 | D_P28 | 0.1541 | L_P28 | 75 | e_P28 | 0.00025 | n51 | P_n51_n47 | 177391.4287 | Pa | = P_n24 - dPt_J46 - dP_P13 - dP_HE11 - dP_P51 - dP_OP5 - dP_P25 - dPt_J50 | J41 | dPt_J41 | 329.4905 | Pa | =DividingSharpEdgedJunctionCircularCrossSection_StraightBranch_dP(Db_J41;Dt_J41;Q_42;Q_29;A_J41;Rho;Nu;2;Cd;Z50;Z50)
P29 | D_P29 | 0.1541 | L_P29 | 25 | e_P29 | 0.00025 | n51 | P_n51_n48 | 177391.4269 | Pa | = P_n27 - dPr_J49 - dP_P33 - dPb_J50 | J46 | dPt_J46 | 41.7557 | Pa | =DividingSharpEdgedJunctionCircularCrossSection_StraightBranch_dP(Db_J46;Dt_J46;Q_31;Q_11;A_J46;Rho;Nu;2;Cd;Z51;Z51)
P30 | D_P30 | 0.1541 | L_P30 | 20 | e_P30 | 0.00025 | [5 empty] | J50 | dPt_J50 | 547.3895 | Pa | =CombiningSharpEdgedJunctionCircularCrossSection_StraightBranch_dP(Db_J50;Dt_J50;Q_33;Q_11;A_J50;Rho;Nu;2;Cd;Z52;Z52)
P32 | D_P32 | 0.1541 | L_P32 | 15 | e_P32 | 0.00025 | n53 | P_n53_n55 | 167783.6497 | Pa | = P_n23_59 - dP_P27 - dPb_J55 | J52 | dPt_J52 | 1085.5546 | Pa | =CombiningSharpEdgedJunctionCircularCrossSection_StraightBranch_dP(Db_J52;Dt_J52;Q_19;Q_34;A_J52;Rho;Nu;2;Cd;Z53;Z53)
P33 | D_P33 | 0.1541 | L_P33 | 25 | e_P33 | 0.00025 | n53 | P_n53_n29 | 167783.6473 | Pa | = P_n54_28 - dP_P35 - dPt_J55 | J53 | dPt_J53 | 27.7278 | Pa | =DividingSharpEdgedJunctionCircularCrossSection_StraightBranch_dP(Db_J53;Dt_J53;Q_28;Q_12;A_J53;Rho;Nu;2;Cd;Z54;Z54)
P34 | D_P34 | 0.1541 | L_P34 | 25 | e_P34 | 0.00025 | [5 empty] | J55 | dPt_J55 | 2818.0759 | Pa | =CombiningSharpEdgedJunctionCircularCrossSection_StraightBranch_dP(Db_J55;Dt_J55;Q_27;Q_35;A_J55;Rho;Nu;2;Cd;Z55;Z55)
P35 | D_P35 | 0.1541 | L_P35 | 25 | e_P35 | 0.00025 | n54 | P_n54_n50 | 178005.2321 | Pa | = P_n43_39 - dP_P19 - dPb_J52 | J56 | dPt_J56 | 547.3895 | Pa | =CombiningSharpEdgedJunctionCircularCrossSection_StraightBranch_dP(Db_J56;Dt_J56;Q_28;Q_12;A_J56;Rho;Nu;2;Cd;Z56;Z56)
P42 | D_P42 | 0.1541 | L_P42 | 10 | e_P42 | 0.00025 | n54 | P_n54_n28 | 178005.0255 | Pa | = P_n27 - dPl_J49 - dP_P34 - dPt_J52 | Branch (Pa)
P48 | D_P48 | 0.1541 | L_P48 | 15 | e_P48 | 0.00025 | [5 empty] | J41 | dPb_J41 | 5086.3296 | Pa | =DividingSharpEdgedJunctionCircularCrossSection_SideBranch_dP(Db_J41;Dt_J41;Q_42;Q_29;A_J41;Rho;Nu;2;Cd;Z58;Z58)
P51 | D_P51 | 0.1541 | L_P51 | 10 | e_P51 | 0.00025 | n12 | P_n12 | 191194.2229 | Pa | = P_n34 - dPb_J41 - dP_P42 | J46 | dPb_J46 | 998.7152 | Pa | =DividingSharpEdgedJunctionCircularCrossSection_SideBranch_dP(Db_J46;Dt_J46;Q_31;Q_11;A_J46;Rho;Nu;2;Cd;Z59;Z59)
[12 empty] | J50 | dPb_J50 | 471.0715 | Pa | =CombiningSharpEdgedJunctionCircularCrossSection_SideBranch_dP(Db_J50;Dt_J50;Q_33;Q_11;A_J50;Rho;Nu;2;Cd;Z60;Z60)
Orifice plate data | [6 empty] | n22 | P_n22 | 175717.803 | Pa | = P_n51_47 - dP_P26 | J52 | dPb_J52 | 2197.377 | Pa | =CombiningSharpEdgedJunctionCircularCrossSection_SideBranch_dP(Db_J52;Dt_J52;Q_19;Q_34;A_J52;Rho;Nu;2;Cd;Z61;Z61)
Name | Pipe diameter (m) | [10 empty] | J53 | dPb_J53 | 914.116 | Pa | =DividingSharpEdgedJunctionCircularCrossSection_SideBranch_dP(Db_J53;Dt_J53;Q_28;Q_12;A_J53;Rho;Nu;2;Cd;Z62;Z62)
OP5 | Dpi_OP5 | 0.1541 |  |  |  |  | n24 | P_n24 | 194188.0725 | Pa | = P_n34 - dPt_J41 - dP_P29 | J55 | dPb_J55 | 1665.8383 | Pa | =CombiningSharpEdgedJunctionCircularCrossSection_SideBranch_dP(Db_J55;Dt_J55;Q_27;Q_35;A_J55;Rho;Nu;2;Cd;Z63;Z63)
OP6 | Dpi_OP6 | 0.1541 | [9 empty] | J56 | dPb_J56 | 471.0715 | Pa | =CombiningSharpEdgedJunctionCircularCrossSection_SideBranch_dP(Db_J56;Dt_J56;Q_28;Q_12;A_J56;Rho;Nu;2;Cd;Z64;Z64)
OP44 | Dpi_OP44 | 0.1541 |  |  |  |  | n27 | P_n27 | 179304.1694 | Pa | = P_n24 - dPb_J46 - dP_P30 - dP_HE31 - dP_P48 - dP_OP47 - dP_P32 | Left (Pa)
OP45 | Dpi_OP45 | 0.1541 | [9 empty] | J14 | dPl_J14 | 2013.2198 | Pa | =SymmetricDividingSharpEdgedTJunctionCircularCrossSection_LeftBranch_dP(Db_J14;Dt_J14;Q_20;Q_21;Rho;Nu;3;Cd;Z66;Z66)
OP47 | Dpi_OP47 | 0.1541 |  |  |  |  | n31 | P_n31 | 221364.418 | Pa | = P_n30_37 + P_Pp36 | J43 | dPl_J43 | 1220.2283 | Pa | =SymmetricCombiningSharpEdgedTJunctionCircularCrossSection_LeftBranch_dP(Db_J43;Dt_J43;Q_20;Q_21;Rho;Nu;2;Cd;Z67;Z67)
[12 empty] | J49 | dPl_J49 | 202.5117 | Pa | =SymmetricDividingSharpEdgedTJunctionCircularCrossSection_LeftBranch_dP(Db_J49;Dt_J49;Q_34;Q_33;Rho;Nu;3;Cd;Z68;Z68)
Junction data | [6 empty] | n34 | P_n34 | 199058.8047 | Pa | = P_n31 - dP_P7 | Right (Pa)
Name | Through diameter (m) |  | Branch diameter (m) |  | Angle(°) | [6 empty] | J14 | dPr_J14 | 2013.2198 | Pa | =SymmetricDividingSharpEdgedTJunctionCircularCrossSection_RightBranch_dP(Db_J14;Dt_J14;Q_20;Q_21;Rho;Nu;3;Cd;Z70;Z70)
J14 | Dt_J14 | 0.1541 | Db_J14 | 0.1541 | A_J14 | 90 | [5 empty] | J43 | dPr_J43 | 1220.2283 | Pa | =SymmetricCombiningSharpEdgedTJunctionCircularCrossSection_RightBranch_dP(Db_J43;Dt_J43;Q_20;Q_21;Rho;Nu;2;Cd;Z71;Z71)
J41 | Dt_J41 | 0.1541 | Db_J41 | 0.1541 | A_J41 | 90 | [5 empty] | J49 | dPr_J49 | 371.8367 | Pa | =SymmetricDividingSharpEdgedTJunctionCircularCrossSection_RightBranch_dP(Db_J49;Dt_J49;Q_34;Q_33;Rho;Nu;3;Cd;Z72;Z72)
J43 | Dt_J43 | 0.1541 | Db_J43 | 0.1541 | A_J43 | 90
J46 | Dt_J46 | 0.1541 | Db_J46 | 0.1541 | A_J46 | 90 | [5 empty] | Pump Head:
J49 | Dt_J49 | 0.1541 | Db_J49 | 0.1541 | A_J49 | 90 | [5 empty] | Pp36 | H_Pp36 | 11.398 | m | =SplineInterpolation(Q_36;D92:D102;E92:E102;Cd)
J50 | Dt_J50 | 0.1541 | Db_J50 | 0.1541 | A_J50 | 90 | [5 empty] | Pump Pressure:
J52 | Dt_J52 | 0.1541 | Db_J52 | 0.1541 | A_J52 | 90 | [5 empty] | Pp36 | P_Pp36 | 111575.3594 | Pa | =StaticPressure_H_Rho_g(H_Pp36;Rho)
J53 | Dt_J53 | 0.1541 | Db_J53 | 0.1541 | A_J53 | 90
J55 | Dt_J55 | 0.1541 | Db_J55 | 0.1541 | A_J55 | 90
J56 | Dt_J56 | 0.1541 | Db_J56 | 0.1541 | A_J56 | 90
Heat-Exchanger data
Name | Diameter (m) |  | Pressure loss coef. ()
HE11 | D_HE11 | 0.1541 | K_HE11 | 0.2
HE12 | D_HE12 | 0.1541 | K_HE12 | 0.2
HE20 | D_HE20 | 0.1541 | K_HE20 | 0.2
HE21 | D_HE21 | 0.1541 | K_HE21 | 0.2
HE31 | D_HE31 | 0.1541 | K_HE31 | 0.2
Pump
Flowrate | Head
(m³/s) | (m fluid)
0 | 15.7
0.0097216 | 16.352
0.019444 | 16.576
0.029166 | 16.128
0.038888 | 15.232
0.048611 | 14.112
0.058333 | 12.544
0.066111 | 11.2
0.077778 | 8.96
0.088889 | 6.72
0.12 | 0
Heat Exchangers
Flowrate | Press. loss
(m³/s) | (Pa)
0 | 0
0.0025 | 1.7935
0.005 | 7.1741
0.0075 | 16.1418
0.01 | 28.6966
0.0125 | 44.8384
0.015 | 64.5673
0.0175 | 87.8832
0.02 | 114.7863
0.0225 | 145.2764
0.025 | 179.3535